## Steamers
WATER USE AND FILTERS FOR CLEVELAND STEAMERS
|  | MAXIMUM FLOW RATE * |  |  | OPTIPURE SIZING RECOMMENDATIONS
MODEL | INTIAL FILL AT START UP (Gallons) | MAX GAL./MIN | MAX GAL./HOUR | MAX GAL./DAY (8 Hour Day) | OPTIPURE MODEL | OPTIONAL OPTIPURE MODEL (No Chloramine)at or below 8.5 ph, +170PPM | SUGGESTED FILTER CHANGE FREQUENCY | OPTIONAL REVERSE OSMOSIS OPTIPURE MODEL | RO PRODUCTION GPD OPTIMAL (77 F) | STORAGE TANK CAPACITY | CURRENT EVERPURE MODEL
STEAMCHEF SERIES (BOILERLESS)
22CET3.1 - Energy Star | 1.1 | 0.066667 | 4 | 32 | QTI1+CR | QTSX-2PG | ANNUAL | OP175/16 | 175 | 16 | 9797-50CT
22CET6.1 - Energy Star | 1.1 | 0.066667 | 4 | 32 | QTI1+CR | QTSX-2PG | ANNUAL | OP175/16 | 176 | 16 | 9797-50CT
22CGT3.1 - Energy Star | 1.1 | 0.066667 | 4 | 32 | QTI1+CR | QTSX-2PG | ANNUAL | OP175/16 | 177 | 16 | 9797-50CT
22CGT6.1 - Energy Star | 1.1 | 0.066667 | 4 | 32 | QTI1+CR | QTSX-2PG | ANNUAL | OP175/16 | 165 | 16 | 9797-50CT
STEAMCRAFT-COUNTER TOP (GENERATORS) | [6 empty] | ANNUAL
21CET8 | 2.8 | 0.057 | 3.42 | 27.36 | QTI1+CR | QTSX-2PG | ANNUAL | OP175/16 | 175 | 16 | 9797-50CT
21CET16 | 3.8 | 0.113 | 6.78 | 54.24 | QTI1+CR | QTSX-2PG | ANNUAL | OP350/16 | 175 | 16 | 9797-50CT
21CGA5 | 4 | 0.113 | 6.78 | 54.24 | QTI1+CR | QTSX-2PG | ANNUAL | OP350/16 | 175 | 16 | 9797-50CT
6-10 PAN MODELS (GENERATORS)
24CGA6.2S | 3.3 | 0.126 | 7.6 | 60.8 | QTI1+CR | QTSX-2PG | ANNUAL | OP350/16 | 350 | 16 | CWT06
24CGA6.2SES Energy Star | 3.3 | 0.096667 | 5.8 | 46.4 | QTI1+CR | QTSX-2PG | ANNUAL | OP175/16 | 175 | 16 | CWT06
24CGA10 | 7.9 | 0.185 | 11.1 | 88.8 | QTI1+CR | QTSX-2PG | 6 MONTHS | OP350/50 | 350 | 50 | CWT06
24CGA10.2 | 3.3 | 0.194 | 11.64 | 93.12 | QTI1+CR | QTSX-2PG | 6 MONTHS | OP350/50 | 350 | 50 | CWT06
24CGA10.2ES Energy Star | 3.3 | 0.13167 | 7.9 | 63.2 | QTI1+CR | QTSX-2PG | 6 MONTHS | OP350/16 | 350 | 16 | CWT06
24CEA10 | 3.8 | 0.113 | 13.56 | 108.48 | QTI1+CR | QTSX-2PG | 6 MONTHS | OP350/50 | 350 | 50 | CWT06
24CGP10 | 16 | 0.36 | 21.6 | 172.8 | QTI1+CR | QTSX-2PG | 3 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
CLASSIC CONVECTION SERIES (BOILER BASE)
200,000 BTU Boilers (24CGM200) | 8 | 0.25 | 15 | 120 | QTI1+CR | QTSX-2PG | 6 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
300,000 BTU Boilers (36CGM300, 36CGM16300) | 12 | 0.36 | 21.6 | 172.8 | QTI1+CR | QTSX-2PG | 3 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
24 kW Boilers (24CEM24) | 9 | 0.16 | 9.6 | 76.8 | QTI1+CR | QTSX-2PG | 6 MONTHS | OP350/50 | 350 | 50 | CWT06
36kW Boilers (24CEM36) | 9 | 0.24 | 14.4 | 115.2 | QTI1+CR | QTSX-2PG | 6 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
48 kW Boilers (24CEM48) | 9 | 0.3 | 18 | 144 | QTI1+CR | QTSX-2PG | 3 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
CLASSIC PRESSURE SERIES (BOILER BASE)
24 kW Boilers PEM24 | 9 | 0.16 | 9.6 | 76.8 | QTI1+CR | QTSX-2PG | 6 MONTHS | OP350/50 | 350 | 50 | CWT06
36kW Boilers PEM36 | 9 | 0.24 | 14.4 | 115.2 | QTI1+CR | QTSX-2PG | 6 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
48 kW Boilers PEM48 | 9 | 0.3 | 18 | 144 | QTI1+CR | QTSX-2PG | 3 MONTHS | BWS1500/50 | 1400 | 50 | CWT06
* Max Flow Rate is when steamer is cooking continuously. Idle mode uses significantly less water.
Guidelines for Recommending a Blended RO Filter.
Get a water quality test. Contact Cleveland Customer Service to order a H2O Test Express Kit, Part number 180-80181
Compare water test against recommended Water Quality Settings below.
If incoming waterr pressure is below 50 PSI, a booster pump maybe required to increase production
Filter Models listed here do not remove Chlorides. A system with reverse osmosis is required to remove harmful chlorides.
NEW WATER QUALITY REQUIREMENTS
TDS: 50-250 ppm
Hardness: 50 - 200 mm (3 - 12 gpg)
pH value: 7.0 - 8.5
CL (Chloride): max 50 ppm
Cl2 (free chlorine): max 0.1 ppm
Fe (iron): max 0.1 ppm
SiO2 (silica): max 13 ppm
NH2Cl (monochloramine): max 0.1 ppm
Water Pressure 35 - 80 PSI
Temperature: max 104oF.